## Commercial
Heat Loss Calculation Worksheet-Commercial
Based on Modine Publication 75-202.7, Heat Loss Calculation-Unit Heaters
Revision 2, Updated 8/21/09
Design Outdoor Temperature °F |  |  |  | -15
Design Indoor Temperature °F |  |  |  | 65
Design Temperature Difference °F |  |  |  | 80
Wall Dimensions (in Feet)
| Length | Height |  | Ft.²
North | 20 | 9 |  | 82
South | 20 | 9 |  | 174
East | 30 | 9 |  | 264
West | 30 | 9 |  | 264
|  |  | Total | 784
| Heat Loss Coefficient |  |  | 0.23
| Heat Loss-Walls |  |  | 14425.6 | Btu/hr.
Wall Heat Loss Coefficients
Poured Concrete 80 lbs./ft.³ 8-in. Thick | [6 empty] | 0.25
Poured Concrete 80 lbs./ft.³ 12-in. Thick | [6 empty] | 0.18
Gravel Aggregate 8-in. Thick | [6 empty] | 0.52
Gravel Aggregate 12-in. Thick | [6 empty] | 0.47
Concrete Block Hollow Cinder Aggrgate 8-in. Thick | [6 empty] | 0.39
Concrete Block Hollow Cinder Aggrgate 12-in. Thick | [6 empty] | 0.36
Concrete Block, w/4-in. Facebrick Gravel 8-in. Thick | [6 empty] | 0.41
Concrete Block, w/4-in. Facebrick Cinder 8-in. Thick | [6 empty] | 0.33
Metal, Uninsulated | [6 empty] | 1.17
Metal w/1-in. Blanket Insulation | [6 empty] | 0.22
Metal w/3-in. Blanket Insulation | [6 empty] | 0.08
Frame, 2x4 w/ ½-in. Asphalt Sheathing, Wood Siding, ½-in. Gypsum Wallboard, Uninsulated | [6 empty] | 0.23
Frame, 2x4 w/ ½-in. Asphalt Sheathing, Wood Siding, ½-in. Gypsum Wallboard, 3-in. Insulation | [6 empty] | 0.07
Window Dimensions (in Feet)
| Length | Height | Quantity | Ft.²
North | 0 | 0 | 0 | 0
South | 3 | 2 | 1 | 6
East | 3 | 2 | 1 | 6
West | 3 | 2 | 1 | 6
|  |  | Total | 18
| Heat Loss Coefficient |  |  | 0.25
| Heat Loss-Windows |  |  | 360 | Btu/hr.
Window Heat Loss Coefficients
Vertical, Single Glass |  |  |  | 0.25
Vertical, Double Glass, 3/16-in. Air Space |  |  |  | 0.18
Horizontal, Single Glass (Sky Light) |  |  |  | 0.52
Door Dimensions (in Feet)
| Length | Height | Quantity | Ft.²
North | 7 | 7 | 2 | 98
South | 0 | 0 | 0 | 0
East | 0 | 0 | 0 | 0
West | 0 | 0 | 0 | 0
|  |  | Total | 98
| Heat Loss Coefficient |  |  | 1.2
| Heat Loss-Doors |  |  | 9408 | Btu/hr.
Door Heat Loss Coefficients
Metal, Single Sheet |  |  |  | 1.2
Wood, 1-in. |  |  |  | 0.64
Wood, 3-in. |  |  |  | 0.43
Floor Dimensions (in Feet)
| Length | Width |  | Exposed Length
| 20 | 30 |  | 100
|  |  | F Factor | 50
| Heat Loss-Floor |  |  | 5000 | Btu/hr.
Floor F Facors
No Insulation | [5 empty] | 50
24-in. Thick, R=3.75 Insulation, -15° F to -19° F Design Temperature | [5 empty] | 43
24-in. Thick, R=3.75 Insulation, -5° F to -9° F Design Temperature | [5 empty] | 38
18-in. Thick, R=3.75 Insulation, 6° F to 10° F Design Temperature | [5 empty] | 31
12-in. Thick, R=3.75 Insulation, 11° F to 15° F Design Temperature | [5 empty] | 31
Roof Dimensions (in Feet)
| Length | Height |  | Ft.²
| 30 | 25 |  | 750
| Heat Loss Coefficient |  |  | 0.75
| Heat Loss-Roof |  |  | 45000 | Btu/hr.
Roof Heat Loss Coefficients
Corrugated Metal Uninsulated | [5 empty] | 1.5
Corrugated Metal w/1-in. Bolt or Blanket Insulation | [5 empty] | 0.23
Corrugated Metal w/1½-in. Bolt or Blanket Insulation | [5 empty] | 0.16
Corrugated Metal w/3-in. Bolt or Blanket Insulation | [5 empty] | 0.08
Flat Metal w/⅜-in. Built-Up Roofing | [5 empty] | 0.9
Flat Metal w/1-in. Blanket Insulation Under Deck | [5 empty] | 0.21
Flat Metal w/2-in. Blanket Insulation Under Deck | [5 empty] | 0.12
Wood, 1-in. w/⅜-in. Built-Up Roofing, Uninsulated | [5 empty] | 0.48
Wood, 1-in. w/1-in. Blanket Insulation | [5 empty] | 0.17
Wood, 2-in. w/⅜-in. Built-Up Roofing, Uninsulated | [5 empty] | 0.32
Wood, 2-in. w/1-in. Blanket Insulation | [5 empty] | 0.15
Concrete Slab, 2-in. w/⅜-in. Built-Up Roofing, Uninsulated | [5 empty] | 0.3
Concrete Slab, 2-in. w/1-in. Insulation Board | [5 empty] | 0.16
Concrete Slab, 3-in. w/⅜-in. Built-Up Roofing, Uninsulated | [5 empty] | 0.23
Concrete Slab, 3-in. w/1-in. Insulation Board | [5 empty] | 0.14
Gypsum Slab, 2-in. w/⅜-in. Built-Up Roofing, Uninsulated | [5 empty] | 0.36
Gypsum Slab, 2-in. w/1-in. Insulation Board | [5 empty] | 0.2
Gypsum Slab, 3-in. w/⅜-in. Built-Up Roofing, Uninsulated | [5 empty] | 0.3
Gypsum Slab, 3-in. w/1-in. Insulation Board | [5 empty] | 0.18
Cubic Volume (in Feet)
| Length | Height | Height | Ft.³
| 20 | 30 | 15 | 9000
| Air Changes per Hour |  |  | 1.25
| Heat Loss-Cubic Volume |  |  | 16363.6364 | Btu/hr.
Estimated Air Changes per Hour Due to Infiltration
Loose Buildings (Older Construction, Single Windows, Uninsulated Doors & Walls, Insulated Roof, Frequently Opened Doors) | [7 empty] | 1.5
Medium Buildings (Newer Construction, Single Windows, Uninsulated Doors, Insulated Walls & Roof, Doors Open Less Frequently) | [7 empty] | 1
Tight Buildings (New Construction, Double Windows, Insulated Doors, Walls & Roof, Doors Opened Infrequently) | [7 empty] | 0.75
Add 10% for Exposure to Prevailing Winds (North or West Walls)
|  |  | Ft.² | Btu/hr.
Wall |  |  | 82 | 150.88
Windows |  |  | 0 | 0
Doors |  |  | 98 | 940.8
| Heat Loss-Prevailing Winds |  |  | 1091.68 | Btu/hr.
|  | Total Heat Loss |  | 91648.9164 | Btu/hr.

## Greenhouse
Heat Loss Calculation Worksheet-Greenhouse
Based on ANSI/ASAE EP406.4, January 2003
Revision 2, Updated 8/21/09
Customer: Sportels
Design Outdoor Temperature °F |  |  | 2
Design Indoor Temperature °F |  |  | 70
Design Temperature Difference °F |  |  | 68
Peak Type Greenhouses
Dimensions in Feet | Width | Peak Height | Eave Height | Length
| 63 | 18 | 14 | 228
End Wall Area (One End Wall) |  | 1008 | Feet²
Side Wall Area |  | 6384 | Feet²
Roof Area |  | 14479.3464 | Feet²
Total Surface Area |  | 22879.3464 | Feet²
Floor Area |  | 14364 | Feet²
Total Volume |  | 229824 | Feet³
Heat Transmission Coefficient |  | 0.7 | Btu/Hr./Ft.²
Construction U-Factor Multiplier |  | 1.01
Infiltration Rate |  | 1 | Air Changes/Hr.
Heat Loss: Radiation, Conduction, Convection |  |  | 1099947.4572 | Btu/Hr.
Heat Loss: Infiltration |  |  | 284146.0364 | Btu/Hr.
Total Heat Loss |  |  | 1384093.4936 | Btu/Hr.
Arch Type Greenhouses*
*For No Eaves, Eave Height = 0 and Width Must be > (2 x Height)
Dimensions in Feet | Width | Peak Height | Eave Height | Length
| 0 | 0 | 0 | 0
Arch Length |  | #DIV/0! | Feet
End Wall Area (One End Wall) |  | #DIV/0! | Feet²
Total Surface Area |  | #DIV/0! | Feet²
Floor Area |  | 0 | Feet²
Total Volume |  | #DIV/0! | Feet³
Heat Transmission Coefficient |  | 0.7 | Btu/Hr./Ft.²
Construction U-Factor Multiplier |  | 1
Infiltration Rate |  | 1.25 | Air Changes/Hr.
Heat Loss: Radiation, Conduction, Convection |  |  | #DIV/0! | Btu/Hr.
Heat Loss: Infiltration |  |  | #DIV/0! | Btu/Hr.
Total Heat Loss |  |  | #DIV/0! | Btu/Hr.
Wall & Roof Heat Loss Coefficients
Single Glass, Sealed |  |  |  | 1.1
Single Glass, Low Emissivity |  |  |  | 0.95
Double Glass, Sealed |  |  |  | 0.65
Single Plastic |  |  |  | 1.1
Single Polycarbonate, Corrugated |  |  |  | 1.10 - 1.20
Single Fiberglass, Corrugated |  |  |  | 1
Double Polyethylene |  |  |  | 0.7
Double Polyethylene, IR Inhibited |  |  |  | 0.5
Rigid Acrylic, Double Wall |  |  |  | 0.56
Rigid Polycarbonate, Double Wall |  |  |  | 0.56 - 0.63
Rigid Acrylic, 32mm, Panels Filled With Polystyrene Pellets |  |  |  | 0.1
Double Polyethylene Over Glass |  |  |  | 0.5
Single Glass With Thermal Blanket (Closed Only) |  |  |  | 0.7
Double Polyethylene With Thermal Blanket (Closed Only) |  |  |  | 0.44
Construction U-Factor Multipliers
Metal Frame and Glazing System 16 to 24 in. Spacing |  |  |  | 1.08
Metal Frame and Glazing System 48 in. Spacing |  |  |  | 1.05
Fiberglass on Metal Frame |  |  |  | 1.03
Film Plastic on Metal Frame |  |  |  | 1.02
Film or Fiberglass on Wood |  |  |  | 1
Estimated Infiltration Rate
New Contruction, Double Plastic Film |  |  |  | 0.75 - 1.50
New Contruction, Glass or Fiberglass |  |  |  | 0.50 - 1.00
Old Construction, Glass, Good Maintenance |  |  |  | 1.00 - 2.00
Old Construction, Glass, Poor Maintenance |  |  |  | 2.00 - 4.00

## Arch Formulas
Formulas for Calculating Quonset-Type Greenhouse
Given the Width(W), Height (H) & Length (L), The Following Formulas are Used
Example: | W | 0
| H | 0
| L | 0
AE = W/2 |  |  |  | 0 | Feet
CE (Diameter - H) = (W*W)/(4*H) |  |  |  | #DIV/0! | Feet
AO (Radius) = (CE + H)/2 |  |  |  | #DIV/0! | Feet
OE (Apothem) = AO - H |  |  |  | #DIV/0! | Feet
AOE (Angle in Degrees) = arctangent (AE/OE) |  |  |  | #DIV/0! | Degrees
AOB (Central Angle) = AOE*2 |  |  |  | #DIV/0! | Degrees
Sector Area = (AOB/360)*3.14*AO² |  |  |  | #DIV/0! | Feet²
Triangle Area of AOB = OE * AE |  |  |  | #DIV/0! | Feet²
Arc Length = (AOB/180) * 3.14 * AO |  |  |  | #DIV/0! | Feet
Segment Area (End Wall Area) = Sector Area - Triangle Area |  |  |  | #DIV/0! | Feet²
Total Surface Area = (Arc Length * L) + (Segment Area * 2) |  |  |  | #DIV/0! | Feet²
Total Cubic Volume = Segment Area * L |  |  |  | #DIV/0! | Feet³
Central Angle Calculation Steps
|  |  | =AE/OE | #DIV/0!
|  |  | ATAN(AE/OE) in radian | #DIV/0!
|  |  | ATAN(AE/OE) in degrees | #DIV/0! | radians *(180/3.14)
|  |  | multiply by 2 | #DIV/0! | degrees